| Handover Documentation Package |
| --- |
| {Insert Project Name} |
| {Insert Package Title (If more than one package is required)} |
|  | Prepared by: Commissioning Manager |  |  |
|  | Date: |  |  |
| Date of issue: |  | Revision: |  | Copy Number: |  |
| Volume: |  |

Table of Contents

Handover Documentation Package	1

Updated Asset Register	4

Interim Maintenance Copies of Design Documents	5

Spare Equipment	6

Equipment Manuals	7

Certificate of Practical Completion	8

Commissioning Work Package	9

Copies of Inspection and Test Records	10

Maintenance Issue of Design Documents	11

Certificate of Acceptance	12

Test and Certify (TC) Forms and Inspection and Testing Forms (ITF’s)	13

TC 1(a) – Colour Light Signal Test Certificate	14

TC 1(b) – Double Light Signal (LED) Test Certificate	15

TC 1(c) – Single Light Signal (LED) Test Certificate	16

C/TC 1(d) – Train Protection Warning System (TPWS)	17

TC 2(a) – Cable Insulation Test Certificate	19

TC 2(b) – Cable Insulation Test Certificate	20

TC 2(c) – Cable Insulation Test Certificate	21

C/TC 3 – Compliance/Test Certificate – Cables	22

C/TC 4 – Compliance/Test Certificate – Cable Variance	23

TC 5 – Pre-Site Test Certificate	24

TC 6 – Point Operating Test Certificate	25

TC 7 – Location Power Supply Test Certificate	26

TC 8 – Motor Generator Test Certificate	27

TC 9 – Circuit Breaker Test Certificate	28

TC 10 – Level Crossing Test Certificate	29

TC 11 – Ready for Test Certificate	30

ITF 12 – Irregularities Found in Testing	31

Certification Inspection and Testing Checklists	32

ITF 13/0 – Certification Inspection and Test Summary Checklist	33

ITF 13/1(a) – Checklist for Colour Light Signal	34

ITF 13/1(b) – Checklist for LED Colour Light Signal	35

ITF 13/2 – Checklist for Points	36

ITF 13/3 – Checklist for Ground Frames/Electric Releasing Switches	37

ITF 13/5 – Checklist for Track Circuits	38

ITF 13/6 – Checklist for Level Crossing	39

ITF 13/7 – Checklist for Power Supplies	40

ITF 13/10 – Checklist for Timer Relays/Units	41

ITF 13/11 – Checklist for Cables	42

ITF 13/15 – Checklist for Telemetry/Panel Processor	43

ITF 13/16 – Checklist for Control Console/ Indicator Diagram	44

ITF 13/17 – Checklist for Location	45

ITF 13/18 – Checklist for Computer Based Interlockings	46

ITF 13/20 – Checklist for Aspect Sequence	47

ITF 14 – Measuring Instrument/Tool Calibration/Test Record	48

Interface Coordination Plan	49

Typical Signal Sighting Forms	64

Level Crossing Sighting Forms	65

Level Crossing Site Inspection Form	66

Stakeholder Site Inspection and Authority to Commission	68

Gated Pedestrian Crossing Assessment Sheet	69

Level Crossing Location Maintenance Visit Sheet	72

Updated Asset Register

Interim Maintenance Copies of Design Documents

Spare Equipment

Equipment Manuals

Certificate of Practical Completion

Commissioning Work Package

Copies of Inspection and Test Records

Maintenance Issue of Design Documents

| Certificate of Acceptance |
| --- |
| The Project: _________________________________ was commissioned into use on date: ____________ and is accepted |
| Signed: |
| Commissioning Manager | Regional Signalling Representative |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

Test and Certify (TC) Forms and Inspection and Testing Forms (ITF’s)

| TC 1(a) – Colour Light Signal Test Certificate |
| --- |
| Location: |  |  | Record Value and / or Initial each Section as checked |
| Signal No | Primary Volts | Top Green | Top Yellow | Top Red | Bottom Green | Bottom Yellow / RTO | Bottom Red / Marker | Lens Colours Verified | ECR/FCOR Function | Focus To |
|  |  | Secondary Volts | Secondary Volts | Secondary Volts | Secondary Volts | Secondary Volts | Secondary Volts |  | Lamp Out | Filament Fail | m |
| Remarks: |
| Test Equipment Number: |  |
| Certified by: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| TC 1(b) – Double Light Signal (LED) Test Certificate | Record Value and / or Initial each Section as checked |
| --- | --- |
| Location: |  |  | Km: |  |  | Signal No: |  |  | Controlled / Automatic | Repeater / Co-Acting |
| Signal Aspect | Voltage Test | R / R | G / R | G / Y | G / G | Y / R | Y / Y | # |  | Signal Profile & LED Colours Verified | Function / Adjust Lamp Proving | Insulation Test | Focussed to “X” Metres |
| Top Green | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| Top Yellow | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| Top Red | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| Bottom Green | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| Bottom Yellow | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| Bottom Red | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| # | AC Side |  |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |  |
| Notes: | # Add all Subsidiary Aspects, Route Indicators, “A” lights. Check of DC side required (if possible) when a AC voltage across an “off” aspect is significant. |
| Remarks: |  | Test Equipment Number: |
| Certified by: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| TC 1(c) – Single Light Signal (LED) Test Certificate | Record Value and / or Initial each Section as checked |
| --- | --- |
| Location: |  |  | Km: |  |  | Signal No: |  |  | Controlled / Automatic | Repeater / Co-Acting |
| Signal Aspect | Voltage Test | Red / Marker | Yellow | Green | RTO or Low Speed | Shunt / Route Indicator | Distant | Signal Profile & LED Colours Verified | Function / Adjust Lamp Proving | Insulation Test | Focussed to “X” Metres |
|  |  |  |  |  |  |  | Yellow Remove main lamp for marker | Green |  |  |  |  |
| Green | AC Side |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |
| Yellow | AC Side |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |
| Red | AC Side |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |
| Marker | AC Side |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |
| RTO or Low Speed | AC Side |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |
| Shunt | AC Side |  |  |  |  |  |  |  |  |  |  |  |
|  | DC Side |  |  |  |  |  |  |  |  |  |  |  |
| Route Indicator | AC Side (1) |  |  |  |  |  |  |  |  |  |  |  |
|  | AC Side (2) |  |  |  |  |  |  |  |  |  |  |  |
| “A” Light | AC Side (on) |  |  |  |  |  |  |  |  |  |  |  |
|  | AC Side (off) |  |  |  |  |  |  |  |  |  |  |  |
| Notes: | Check of DC side required (if possible) when a AC voltage across an “off” aspect is significant. |
| Remarks: |  | Test Equipment Number: |
| Certified by: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| C/TC 1(d) – Train Protection Warning System (TPWS) |
| --- |
| NUMBER: |  | PROJECT NAME: |  |
| DATE: |  | PROJECT No: |  |
| WEATHER: |  | STAGE No: |  |

| SIGNAL NAME: or (Buffer Stop /Bridge) |  | UP or DN Direction |  |
| --- | --- | --- | --- |
| LOCATION NAME |  | Normal or Wrong Direction |  |

| CONFIGURATION of TPWS EQUIPMENT LIST - TRAIN STOP (TSS) AND OVERSPEED SENSOR (OSS) | How many INSTALLED |
| --- | --- |
| MODULE | COLOUR | PIN CODE | DIRECTION | PART No. | BASEPLATE P/N | ARM kHz | TRIGGER kHz | QTY |
| Power Supply | Red AC-SIM | 1035 | N/A | 604366-20 | N/A | N/A | N/A |  |
| Overspeed | Yellow | 1036 | Normal | 604367-20 | 606630-30 | f1 (64.250) | f2 (65.250) |  |
| TrainStop | Green | 1038 | Normal | 604367-21 | 606630-31 | f3 (66.250) | f2 (65.250) |  |
| Overspeed | Blue | 1037 | Wrong / Reverse | 604367-22 | 606630-32 | f4 (64.750) | f5 (65.750) |  |
| TrainStop | Brown | 1039 | Wrong / Reverse | 604367-23 | 606630-33 | f6 (66.750) | f5 (65.750) |  |

Table 1: TPWS Equipment Types

| Items following to CERTIFY MODULES, BASEPLATE, MEASURING FIELD/SIGNAL STRENGTH TO LOOP AERIAL |
| --- |
| Write the Identification Label as provided by DMS compliant drawings – refer to diagram in Table 4. Write all serial numbers provided to each TPWS equipment. Ensure part numbers align to Table 1. If not contact the ARTC Signal Standards Manager. Measure and record 110Vac voltage to each baseplate termination 1 & 2 (voltage between 88Vac – 121Vac rms). Confirm and operate POWER ON (Green) Lights ON & OFF when power is applied to each TPWS modules (Red, Green, Brown, Yellow & Blue). Red Module – Operate LOOPS ACTIVE lights when loop aerials are energised and operating. The TSS Green/Brown Module – Operate MAIN I/P / MAIN SIGNAL lights (yellow LED) when signalling system request loop aerial energisation (red aspect). The TSS Green/Brown Module – SUPP I/P / SUB SIGNAL lights (yellow LED) (clear aspect) is ON when signalling system suppresses loop aerial energisation (overrides MAIN I/P). The OSS Yellow/Blue Module – Operate MAIN I/P lights (yellow LED) when signalling system request loop aerial energisation (red Aspect). The OSS Yellow/Blue Module – SUPP I/P / SUB SIGNAL lights (yellow LED) (clear aspect) is ON when signalling system suppresses loop aerial energisation (overrides MAIN I/P). The Yellow/Green/Blue/Brown Module – FAULT lights (red LED) if a loop aerial is disconnected or not driven correctly (i.e. disconnect outgoing terminal) - (Latches ON; reset by power-off then repowering the unit – wait 5 seconds). Table 2 is considered internal test and Table 3 is considered through test to the Loop Aerial by means of disconnection of PLUG or removing a LINK in the TPWS trackside disconnection box. |
| Items | Red AC-SIM PSU 1 | Baseplate | TSS Green / Brown Module | Red AC-SIM PSU 2 | Baseplate | OSS Yellow / Blue Module |
| A: Label | (Identification) ① & ② See diagram in Table 4: | (Identification) ③ See diagram in Table 4: |
| B: Serial No. |  |  |  |  |  |  |
| C: | Measure across 1 & 2 of Baseplate: | Vac | Measure across 1 & 2 of Baseplate: | Vac |
| Items | Red AC-SIM PSU 3 | Baseplate | OSS Yellow / Blue Module | Red AC-SIM PSU 4 | Baseplate | OSS Yellow / Blue Module |
| A: Label | (Identification) ④ & ⑤ See diagram in Table 4: | (Identification) ⑥ & ⑦ See diagram in Table 4: |
| B: Serial No. |  |  |  |  |  |  |
| C: | Measure across 1 & 2 of Baseplate: | Vac | Measure across 1 & 2 of Baseplate: | Vac |
| Task/Items D, E, F, G, H, I & J: | Items identified are functionally tested, meets the design requirements and can be found as per listed drawing sheets number following completing this task: List sheet Numbers: - |

Table 2: TPWS Module Test & Light Indicators to Loop Aerial field Strengths

| Items following to certify CONFIGURATION of TPWS LOOP AERIAL / ANTENNA & TAIL CABLE |
| --- |
| Identify Each Loop Aerial | ① Trigger | ② Arming | ③ Arming | ④ Trigger | ⑤ Arming | ⑥ Trigger | ⑦ Arming |
| Loop Aerial Part Number: |  |  |  |  |
| Loop Aerial Serial Numbers |  |  |  |  |  |  |  |
| Loop Aerial Mod No. |  |  |  |  |  |  |  |
| Height (mm) between top of rail to top of Loop Aerial | Check Height of Loop Aerials are to be between 60 to 100 mm below top of rail – Record figures |
|  | mm | mm | mm | mm | mm | mm | mm |
| Wheel Measurements | (Longitudinal Tolerance = + / - 10mm). (d0 = between 0 – 3.5m). (d1, d2, d3, d4, d5 = +/-0.5mm) Look to Diagram TABLE 4 for guidance. RECORD metre distances d0, d1, d2, d3, d4 & d5. |
|  | d0= |  | d1= | d2= | d3= | d4= | d5= |
|  | m |  | m | m | m | m | m |
| Accepting measurements d0, d1, d2, d3, d4 & d5 has meet the design requirements to SAP and Bonding Plan and can be found per listed drawing sheets number following completing this task: List sheet Numbers: - |
| Signal Strength Measurement | Place the maintenance jig across of the centre of the loop aerial and insert the test aerial. Record value. Note: frequencies have tolerance of +/- 5 Hz. |
| Measured Frequency (kHz) must be within 0.01kHz | kHz | kHz | kHz | kHz | kHz | kHz | kHz |
| Measure Signal Strength | Measure the Signal strength, which must be NO LESS than 29mV but no greater than 53mVac. |
| Energised Loop (mV) (Range 29mVac – 53mVac) | mV | mV | mV | mV | mV | mV | mV |
| Measure Field Interference | Measure the Field strength, which must be NO MORE than 2mV on the 50mVac range. |
| De-energised Loop (mV) (Less Than 2mV) | mV | mV | mV | mV | mV | mV | mV |
| Observe Fail Indication LED: | Test; either disconnect LINK (TPWS disconnection box) or PLUG (loop aerial) to ensure FAULT Lights come ON the Yellow/Green/Blue/Brown Module. Mark below which test was conducted; LINK or PLUG. |
| Plug / Link |  |  |  |  |  |  |  |
| Tail Cable Sizes: INSERT the tail cable size (m) installed – p/n 606777-12 (10m), p/n 606777-03 (35m), p/n 606777-04 (15m) |
| Cable - 10 m, 35 m or 15 m | m | m | m | m | m | m | m |

Table 3: TPWS Loop Aerial Testing & Certifications.

|  | ITEM | Serial No | Expire Date |
| --- | --- | --- | --- |
|  | Meter |
|  | Aerial |
|  | Commissioning Jig |
|  | Maintenance Jig |

Table 4: Reference / Method & Test Tools Records

| Table 1 & 2 CERTIFIED BY: |  |  | Date: | Position |
| --- | --- | --- | --- | --- |
| Name / Surname (Print): | Initials: | Signature: |  |

| Table 3 & 4 CERTIFIED BY: |  |  | Date: | Position |
| --- | --- | --- | --- | --- |
| Name / Surname (Print): | Initials: | Signature: |  |

| TC 2(a) – Cable Insulation Test Certificate |  | Certificate No: |  |
| --- | --- | --- | --- |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Cable Type: |  | No of Cores: |  | Specification No: |  |
| From Location: |  | To Location: |  | Cable Name: |  |
| Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core |
|  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |
| Shield |  |  |  |  | 17 |  |  |  |  | 34 |  |  |  |  |
| 1 |  |  |  |  | 18 |  |  |  |  | 35 |  |  |  |  |
| 2 |  |  |  |  | 19 |  |  |  |  | 36 |  |  |  |  |
| 3 |  |  |  |  | 20 |  |  |  |  | 37 |  |  |  |  |
| 4 |  |  |  |  | 21 |  |  |  |  | 38 |  |  |  |  |
| 5 |  |  |  |  | 22 |  |  |  |  | 39 |  |  |  |  |
| 6 |  |  |  |  | 23 |  |  |  |  | 40 |  |  |  |  |
| 7 |  |  |  |  | 24 |  |  |  |  | 41 |  |  |  |  |
| 8 |  |  |  |  | 25 |  |  |  |  | 42 |  |  |  |  |
| 9 |  |  |  |  | 26 |  |  |  |  | 43 |  |  |  |  |
| 10 |  |  |  |  | 27 |  |  |  |  | 44 |  |  |  |  |
| 11 |  |  |  |  | 28 |  |  |  |  | 45 |  |  |  |  |
| 12 |  |  |  |  | 29 |  |  |  |  | 46 |  |  |  |  |
| 13 |  |  |  |  | 30 |  |  |  |  | 47 |  |  |  |  |
| 14 |  |  |  |  | 31 |  |  |  |  | 48 |  |  |  |  |
| 15 |  |  |  |  | 32 |  |  |  |  | 49 |  |  |  |  |
| 16 |  |  |  |  | 33 |  |  |  |  | 50 |  |  |  |  |
| Weather Conditions: | Wet / Damp / Dry |  | Wire Count on each cable core termination correct: | Yes / No |
| Remarks |  | Test Equipment No: |
| Note: Where insulation values are greater than the minimum value, boxes may be ticked. Actual value entries must be made where the figure is less than the minimum value, viz… Core to core 100 M, (60 Mohm/km if cable > 500 m long) Core to Shield 100 M, (60 Mohm/km if cable >500 m long); Shield to Earth 10 M, (5 Mohm/km if cable > 500 m long) |
| Work Status Statement | Received/Checked/Action Statement |
| The Insulation tests described above have been performed and the results recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| TC 2(b) – Cable Insulation Test Certificate |  | Certificate No: |  |
| --- | --- | --- | --- |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Cable Type: |  | Cable Type: |  | Cable Type: |  |
| No of Cores: |  | No of Cores: |  | No of Cores: |  |
| From: |  | To: |  | From: |  | To: |  | From: |  | To: |  |
| Cable Name: |  | Cable Name: |  | Cable Name: |  |
| Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core |
|  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |
| Shield |  |  |  |  | Shield |  |  |  |  | Shield |  |  |  |  |
| 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |
| 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  |
| 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  |
| 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  |
| 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  |
| 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  |
| Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core |
|  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |
| Shield |  |  |  |  | Shield |  |  |  |  | Shield |  |  |  |  |
| 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |
| 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  |
| 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  |
| 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  |
| 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  |
| 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  |
| Weather Conditions: | Wet / Damp / Dry |  | Wire Count on each cable core termination correct: | Yes / No |
| Remarks |  | Test Equipment No: |
| Note: Where insulation values are greater than the minimum value, boxes may be ticked. Actual value entries must be made where the figure is less than the minimum value, viz… Core to core 100 M, (60 Mohm/km if cable > 500 m long) Core to Shield 100 M, (60 Mohm/km if cable >500 m long); Shield to Earth 10 M, (5 Mohm/km if cable > 500 m long) |
| Work Status Statement | Received/Checked/Action Statement |
| The Insulation tests described above have been performed and the results recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| TC 2(c) – Cable Insulation Test Certificate |  | Certificate No: |  |
| --- | --- | --- | --- |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Cable Type: |  | Cable Type: |  | Cable Type: |  |
| No of Cores: |  | No of Cores: |  | No of Cores: |  |
| From: |  | To: |  | From: |  | To: |  | From: |  | To: |  |
| Cable Name: |  | Cable Name: |  | Cable Name: |  |
| Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core | Core No | Continuity | Insul | Resist To | Core |
|  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |  |  | Core | Shield | Earth |
| Shield |  |  |  |  | Shield |  |  |  |  | Shield |  |  |  |  |
| 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  |
| 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  |
| 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  |
| 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  |
| 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  |
| 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  |
| 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  |  |  |
| 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  |  |  |
| 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  |  |  |
| 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  |  |  |
| 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  |  |  |
| 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  |
| 13 |  |  |  |  | 13 |  |  |  |  | 13 |  |  |  |  |
| 14 |  |  |  |  | 14 |  |  |  |  | 14 |  |  |  |  |
| 15 |  |  |  |  | 15 |  |  |  |  | 15 |  |  |  |  |
| Weather Conditions: | Wet / Damp / Dry |  | Wire Count on each cable core termination correct: | Yes / No |
| Remarks |  | Test Equipment No: |
| Note: Where insulation values are greater than the minimum value, boxes may be ticked. Actual value entries must be made where the figure is less than the minimum value, viz… Core to core 100 M, (60 Mohm/km if cable > 500 m long) Core to Shield 100 M, (60 Mohm/km if cable >500 m long); Shield to Earth 10 M, (5 Mohm/km if cable > 500 m long) |
| Work Status Statement | Received/Checked/Action Statement |
| The Insulation tests described above have been performed and the results recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| C/TC 3 – Compliance/Test Certificate – Cables |  | Sheet No: |  |
| --- | --- | --- | --- |
| Project Location: |  |
| Description: |  |
| Stage No: |  |
| Location: |  |
| Cable / Cable Identification: | Insulation Resistance | Cable Loop Resistance (Ohms) | Polarity Check | Certified By: |
| Size | Type (Cores) | Terminals | Destination | Core to Core (Megohms) | Core to Core (Megohms) |  |  | Initials | Signature | Date |
| Instructions: |
| Insert initials or values to denote activity complete. Insert N/A if the activity is NOT APPLICABLE. Insert date/name/signature when each section is completed. Advise Tester-in-Charge on completion of each form and forward copy for permanent record of testing. |

| C/TC 4 – Compliance/Test Certificate – Cable Variance |  | Sheet No: |  |
| --- | --- | --- | --- |
| This certificate is to be completed for any cable under test where the measured value of insulation or continuity resistance is less than specified OR the value for any individual core deviates by more than 10% when compared with the corresponding value measured for other cores. |
| Project: |  |
| Description: |  |
| Stage No: |  |
| Cable Location: | From |  | to |  |  | Cable Size: |  |
| Terminals: | [ | to | ] |  | [ | to | ] |
| Core No | Insulation Resistance | Continuity Resistance Loop Value [Ohms] | Core No | Insulation Resistance | Continuity Resistance Loop Value [Ohms] |
|  | Core to Earth [Megohms] | Core to Other Cores [Megohms] |  |  | Core to Earth [Megohms] | Core to Other Cores [Megohms] |  |
| 1 |  |  |  | 26 |  |  |  |
| 2 |  |  |  | 27 |  |  |  |
| 3 |  |  |  | 28 |  |  |  |
| 4 |  |  |  | 29 |  |  |  |
| 5 |  |  |  | 30 |  |  |  |
| 6 |  |  |  | 31 |  |  |  |
| 7 |  |  |  | 32 |  |  |  |
| 8 |  |  |  | 33 |  |  |  |
| 9 |  |  |  | 34 |  |  |  |
| 10 |  |  |  | 35 |  |  |  |
| 11 |  |  |  | 36 |  |  |  |
| 12 |  |  |  | 37 |  |  |  |
| 13 |  |  |  | 38 |  |  |  |
| 14 |  |  |  | 39 |  |  |  |
| 15 |  |  |  | 40 |  |  |  |
| 16 |  |  |  | 41 |  |  |  |
| 17 |  |  |  | 42 |  |  |  |
| 18 |  |  |  | 43 |  |  |  |
| 19 |  |  |  | 44 |  |  |  |
| 20 |  |  |  | 45 |  |  |  |
| 21 |  |  |  | 46 |  |  |  |
| 22 |  |  |  | 47 |  |  |  |
| 23 |  |  |  | 48 |  |  |  |
| 24 |  |  |  | 49 |  |  |  |
| 25 |  |  |  | 50 |  |  |  |
| Instructions: |
| Insert initials or values to denote activity complete. Insert N/A if the activity is NOT APPLICABLE. Insert date/name/signature when each section is completed. Advise Tester-in-Charge on completion of a Cable Variance Form and wait for further directions. Advise Tester-in-Charge on completion of each form and forward copy for permanent record of testing. |
| Certified By: |  | Initials: |  |  | Signature: |  |  | Date: |  |

| TC 5 – Pre-Site Test Certificate |  | Certificate No: |  |
| --- | --- | --- | --- |
| WP No: |  |  | Job/Contract No: |  |  | Prepared By: |  |
| Location / Description: |  |
| Test | Tested By: |
|  | Date | Tester’s Signature |
| Apparatus – General Inspection |  |  |
| Wire Count |  |  |
| Null Count |  |  |
| Bell Continuity Test |  |  |
| Insulation Megger Test |  |  |
| Equipment – Not Fitted [Wires run, crimped and labelled] |
| Equipment | Installed | Tested |
|  | Date | Signed | Date | Signed |
| Remarks |
| Circulation: |
| Original – Attached firmly to the equipment in a protective envelope Copy 1 – Commissioning Manager Copy 2 – Testing Engineer Copy 3 – Site Office |

| TC 6 – Point Operating Test Certificate |
| --- |
| Location: |  |  | Tests to be carried out in accordance with Manual |
| Point End | Type * | Operating Voltage | Facing Point Lock | Detection | Run Amps | Slip Amps | Motor Cut Off Time | Operating Time |
|  |  | Normal | Reverse | Normal | Reverse | Normal | Reverse | Normal | Reverse | Normal | Reverse | Sec | Sec |
| Remarks: |
| Team Leader: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Note: | * Type: M – Mech, EM – Elec, CL – Clamp Lock, CW – Claw Lock ** With Induction Motors the difference between running current and slip current may not be measurable. Adjustments for each type of mechanism are given in the equipment manuals. |

| TC 7 – Location Power Supply Test Certificate |
| --- |
| Location: |  |  | Tests to be carried out in accordance with Manual |
|  | Voltage | Current | Volts to Earth Active/Positive | Volts to Earth Common/Negative | Earth Leakage Detectors |  |  |
| 120 V Normal Supply |  |  |  |  | 120 V |  | Eco Test |  |
| 120 V Emergency Supply |  |  |  |  | PTS 120 V |  | Indication Test |  |
| 50 V Channel No1 |  |  |  |  | INT 50 V |  | PSI Warning |  |
| 50 V Channel No2 |  |  |  |  | EXT 50 V |  | PSI Fail |  |
| Remarks: |
| Test Equipment Number: |  |
| Team Leader: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| TC 8 – Motor Generator Test Certificate |
| --- |
|  | Tests to be carried out in accordance with Manual |
| Location | Battery Volts | Cycle Test | Run Meter Hours | Output Voltage | Fuel Tank Level |
|  | Charger On | Charger Off |  |  |  |  |
| Remarks: |
| Test Equipment Number: |  |
| Team Leader: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| TC 9 – Circuit Breaker Test Certificate |
| --- |
| Location: |  |
| C/B Number or Name | C/B Rating Amps | Load Amps | C/B Number or Name | C/B Rating Amps | Load Amps |
| Remarks: |
| Test Equipment Number: |  |
| Team Leader: |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| TC 10 – Level Crossing Test Certificate |
| --- |
| Level Crossing Road Name: |  |  | Location: |  |  | Kilometrage: |  |
| Lamp | Lamp Volts | Lamp Focus | Lamp | Lamp Volts | Lamp Focus | Battery Conditions | Load Conditions | Bell |
| A |  |  | SS TIP |  |  | Alarm Card Setting |  | Standing Load Amps |  | Sydney Side Volts |  |
| B |  |  | 1 |  |  | Bus Volts ** |  | Operating Load Amps |  | Country Side Volts |  |
| C |  |  | 2 |  |  | Charge Amps ** |  | Gates Rise Seconds |  | Timer Adjustment |  |
| D |  |  | CS TIP |  |  | Battery Record Card Complete |  | Gates Lower Seconds |  | Contact Adjustment |  |
| E |  |  | 1 |  |  | Charger Tapping (Where Applicable) |  | Gates Delay Seconds |  | Signs |
| F |  |  | 2 |  |  |  |  | Battery Volts ## |  | Up Side Road |  |
| G |  |  | Ped 1 |  |  |  |  |  |  | Down Side Road |  |
| H |  |  | Ped 2 |  |  |  |  |  |  | Up Track |  |
| J |  |  | Ped 3 |  |  |  |  |  |  | Down Track |  |
| K |  |  | Ped 4 |  |  |  |  |  |  |  |  |
| Remarks: |  | Test Equipment Number: |
| Notes: | ** Readings to be taken when charge rate has stabilised ## Switch battery charger off. Take voltage reading. Operate crossing for two (2) minutes and, with the crossing operating, take voltage reading (if gates fitted, with gates rising) |
| Team Leader |
| Name: |  |  | Signature: |  |  | Date: |  |
| Received/Checked/Actioned by: |
| Name: |  |  | Signature: |  |  | Date: |  |

| TC 11 – Ready for Test Certificate |  | Certificate No: |  |
| --- | --- | --- | --- |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Details of Equipment Ready for Test |
| I hereby certify that the signalling detailed above, at |
|  | location: |  |  | at: |  | km |  |
| has been inspected and pre-tested and in every respect is ready for certification testing, there being no outstanding installation work. |
|  | Team Leader Name: |  |  |
|  | Signature: |  |  | Date: |  |  |

| ITF 12 – Irregularities Found in Testing |  | Number: |  |
| --- | --- | --- | --- |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Location/Interlocking Area: |  |
| Design Drawing Reference No: |  |
| Date | Time | Description of Irregularity | Tester’s Signature |
| Issued to Commissioning Manager |
| By Testing Engineer: |  |  | Date: |  |
| Proposed Action to be Taken by Testing Engineer |
| Approved by Commissioning Manager |
| Signature: |  |  | Date: |  |
| Defect Corrected and Certified Correct |
| Team Leader Signature: |  |  | Date: |  |
| Testing Engineer Signature: |  |  | Date: |  |
| Issued to Commissioning Manager |

Certification Inspection and Testing Checklists

| ITF 13/0 – Certification Inspection and Test Summary Checklist |
| --- |
| No | Apparatus | Type Approval | Manufacturer Test Certificate | Apparatus Inspections | Circuit & Insulation Test | Apparatus Function Test | Control & Interlocking Test | Test from Operators Interface | Aspect Sequence Test | Test Documentation | Date | Signature |
|  |  |  |  | General | Warding/ Indexing/ Pin Coding |  |  |  |  |  | Design Drawings | Check Lists | Certificates |  |  |
| 1 | Signals |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Track Circuits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Points |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Ground Frames/Releasing Switches |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Level Crossings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 | Locations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 | Central Interlocking |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | Cables Main |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | Cables Local |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | Panel Processor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 | Local Control Panel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 | Remote Control/Indication |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 | Train Describer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 | Operator Interface |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | Power Supplies Electric |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 16 | Earthing/Surge & Lightning Protection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 | Signal Telephones |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 | Redundant Equipment |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 | Test Copies, Master Test Copies |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Remarks |
| Commissioning Manager - Name: |  |  | Signature: |  |  | Date: |  |

| ITF 13/1(a) – Checklist for Colour Light Signal |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Colour Light Signal |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Anti-phantom devices, site screens, hoods, backgrounds fitted and correct, as applicable. |  |
| 3 | Filament fail relays, flasher units, pulsating units, circuit operation correct. |  |
| 4 | Test Certificate of readings of parameters, completed & correct. |  |
| 5 | Lamp proving relays/modules, circuit operation correct. |  |
| 6 | Cables, cabling, terminations correct. |  |
| 7 | Circuit continuity tests, wire/null counts, correct. |  |
| 8 | Insulation tests, correct. |  |
| 9 | Local circuit function test, correct. |  |
| 10 | Aspects correct and Aspect Sequence Tests correct. (see TC 13/20) |  |
| 11 | No residual voltages on lights when fuse removed. |  |
| 12 | Padlocks, locks fitted and correct. |  |
| 13 | Ladders, landings, cages, secure and correct. |  |
| 14 | Lens systems, colour, spread, deflection sectors, correct. |  |
| 15 | Lamp types, LED types correct. |  |
| 16 | Route indicators, junction repeaters, circuit operation correct. |  |
| 17 | Signal installation as per Approved Signal Sighting Form (attached) |  |
| 18 | Final focus/alignment and sighting correct. |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/1(b) – Checklist for LED Colour Light Signal |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Colour Light LED Signal |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Site screens, hoods, backgrounds fitted and correct, as applicable. |  |
| 3 | Flasher units, pulsating timer adjusted to 640ms “off” & 200ms”on”, circuit operation correct. |  |
| 4 | Test Certificate TC-1 (a),or (b) of readings of parameters, completed & correct. |  |
| 5 | Lamp proving relays/modules, circuit operations correct. |  |
| 6 | Cables, cabling, terminations correct. |  |
| 7 | Circuit continuity tests, wire/null counts, correct. |  |
| 8 | Insulation tests, correct. |  |
| 9 | Local circuit function test, correct. |  |
| 10 | Aspects correct and Aspect Sequence Tests correct. (see TC 13/20) |  |
| 11 | No residual voltages on lights when fuse removed. |  |
| 12 | Padlocks, locks fitted and correct. |  |
| 13 | Ladders, landings, cages, secure and correct. |  |
| 14 | For Operating circuits not utilising twisted pair cabling, conduct “No Volts” tests for each aspect level and with all fuses removed. |  |
| 15 | LED types, indicators/repeaters sizes and colours correct. |  |
| 16 | Route indicators, junction repeaters, stencil indicators circuit operation correct. |  |
| 17 | Signal installation as per Approved Signal Sighting Form (attached) |  |
| 18 | Brightness / Final focus / alignment and sighting correct. |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/2 – Checklist for Points |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Points |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Points operation, including, multiple drives correct. |  |
| 3 | Separate detectors correct. |  |
| 4 | ESML/EOL lock & key, warding/indexing, positioning correct. |  |
| 5 | Point stretcher bars, rodding, tie plates, insulations fitted & correct. |  |
| 6 | Nuts and fittings secured and locked. |  |
| 7 | Facing point lock adjustment and detection test correct. |  |
| 8 | Point switch detection adjustment test correct. |  |
| 9 | Circuit continuity tests, wire/null counts correct. |  |
| 10 | Insulation test correct. |  |
| 11 | Local circuit function test correct. |  |
| 12 | Point correspondence test correct. |  |
| 13 | ESML/EOL & emergency manual operation test correct. |  |
| 14 | ESML/EOL lock contacts operated by key & put signals to stop. |  |
| 15 | Cables, cabling, terminations correct. |  |
| 16 | Test certificate of readings of parameters completed & correct. |  |
| 17 | Point cut-off timer operation correct. |  |
| 18 | Padlocks, locks, fitted and correct. |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/3 – Checklist for Ground Frames/Electric Releasing Switches |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Ground Frames/Electric Releasing Switches |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Lever nameplates correct, notice boards correct. |  |
| 3 | Catchrod contacts, lever rotaries contacts, adjustments correct. |  |
| 4 | Electric lever lock drop contact adjustment correct. |  |
| 5 | Releasing switch rotary contacts, lock drop contact, adjustment correct. |  |
| 6 | Annett locks and keys, warding and inscriptions, correct. |  |
| 7 | Mechanical frame interlocking test, correct. |  |
| 8 | Other mechanical locking, test correct. |  |
| 9 | Dummy bars fitted on interlocking machines, where required. |  |
| 10 | XL locks, SL locks fitted and correct, where applicable. |  |
| 11 | Channel iron rodding runs, secure, correct. |  |
| 12 | Cranks secure and crank adjustments, correct. |  |
| 13 | Releasing switch/ground frame separation correct. |  |
| 14 | Padlocks, locks, fitted and correct. |  |
| 15 | Circuit continuity tests, wire/null counts correct. |  |
| 16 | Insulation tests correct. |  |
| 17 | Local circuit function tests correct. |  |
| 18 | Releasing switch/ground frame operation correct. |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/5 – Checklist for Track Circuits |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Track Circuits |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Track circuit limits, fouling/clearance points, block joints, dead sections, correct. |  |
| 3 | Impedance bonds, electrolysis bonds, spark gaps, traction bonding correct. |  |
| 4 | Track circuit bonding correct. |  |
| 5 | No spurious connections or earths, spark gaps open circuit. |  |
| 6 | Track circuit leads, cables, cabling, terminations correct. |  |
| 7 | Surge protection and earthing correct. |  |
| 8 | Circuit continuity tests, wire/null counts correct. |  |
| 9 | Insulation tests correct. |  |
| 10 | Test certificates of readings of parameters completed and correct. |  |
| 11 | Equal rail currents 50Hz AC double rail track circuits. |  |
| 12 | Polarity/phase reversal between similar type track circuits, correct. |  |
| 13 | Nil/negligible residual receiver/relay voltage when feed fuse removed. |  |
| 14 | Drop away shunt test, fixed shunt tests (all extremities, mid points) correct. |  |
| 15 | Correspondence through tests correct. |  |
| 16 | Track stick circuit operation correct. |  |
| 17 | Padlocks, locks fitted and correct. |  |
| 18 | Occupational Health & Safety/Environmental compliance, correct |  |
| 19 | Workmanship to best practice, equipment in good condition |  |
| 20 | Redundant equipment securely inoperative, made safe/removed. |  |
| 21 | Ready for commissioning into use. |  |
| 22 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/6 – Checklist for Level Crossing |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Level Crossing |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Warning strike in distances correct. |  |
| 3 | Train warning boards, speed boards, penalty notices, road signs & markings, correct. |  |
| 4 | Focus/alignment lights correct. |  |
| 5 | Bells/audible warning devices orientation, sound levels correct. |  |
| 6 | Cables, cabling, terminations correct. |  |
| 7 | Boom/gate mechanisms adjustments correct |  |
| 8 | AC power supply correct. |  |
| 9 | Battery and battery charger adjustment, alarms, PSI’s, correct |  |
| 10 | Test switch operation correct. |  |
| 11 | Emergency switch operation correct |  |
| 12 | Padlocks, security locks fitted and correct |  |
| 13 | Circuit continuity tests, wire/null counts correct |  |
| 14 | Insulation tests correct. |  |
| 15 | Local circuit function tests correct. |  |
| 16 | Operating sequence function test correct. |  |
| 17 | Test Certificate of readings of parameters completed and correct. |  |
| 18 | Operation of LX monitor correct. |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/7 – Checklist for Power Supplies |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Power Supplies |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Fuses & circuit breakers, settings, ratings, discrimination, correct. |  |
| 3 | Surge protection & earthing correct. |  |
| 4 | Earth resistance tests correct. |  |
| 5 | Battery, battery charger adjustment, alarm card adjustment, correct. |  |
| 6 | Test Certificate of reading of parameters completed and correct. |  |
| 7 | Power supply isolation and insulation and freedom from earths, correct. |  |
| 8 | Polarity/phase correct. |  |
| 9 | Voltage regulation & mains voltage drop all loads, test correct. |  |
| 10 | Emergency changeover operation (on line), correct. |  |
| 11 | Uninterruptible power supply operation, correct. |  |
| 12 | Loadings correct, spare capacity correct. |  |
| 13 | Earth leakage detectors adjustment & operation, correct. |  |
| 14 | Mains Failure Plant cut-in & operation, correct. |  |
| 15 | Status indicators and alarms operation, correct. |  |
| 16 | Extra channel of dual channel supports max. load, test correct. |  |
| 17 | Busbars, cables, cabling, terminations, correct. |  |
| 18 |  |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/10 – Checklist for Timer Relays/Units |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Timer Relays/Units |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Actual time tested to specified time, correct, for the following timer relays/units: |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |
| 7 |  |  |
| 8 |  |  |
| 9 |  |  |
| 10 |  |  |
| 11 |  |  |
| 12 |  |  |
| 13 |  |  |
| 14 |  |  |
| 15 |  |  |
| 16 |  |  |
| 17 |  |  |
| 18 |  |  |
| 19 |  |  |
| 20 |  |  |
| 21 |  |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/11 – Checklist for Cables |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Cables |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Spare core availability correct. |  |
| 3 | All ends terminated or properly sealed, no loose wires. |  |
| 4 | Continuity tests, wire/null counts correct. |  |
| 5 | Test Certificate of readings of parameters completed & correct. |  |
| 6 |  |  |
| 7 |  |  |
| 8 |  |  |
| 9 |  |  |
| 10 |  |  |
| 11 |  |  |
| 12 |  |  |
| 13 |  |  |
| 14 |  |  |
| 15 |  |  |
| 16 |  |  |
| 17 |  |  |
| 18 |  |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/15 – Checklist for Telemetry/Panel Processor |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Telemetry/Panel Processor |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Software versions correct. |  |
| 3 | Hardware correct. |  |
| 4 | Start up test correct. |  |
| 5 | Shut down test correct. |  |
| 6 | Power supply interruption test correct. |  |
| 7 | Arbitration test and seamless changeover, correct. |  |
| 8 | Circuit continuity test, wire/null counts correct. |  |
| 9 | Insulation tests correct. |  |
| 10 | Local circuit function tests correct. |  |
| 11 | Correspondence tests, correct. |  |
| 12 | Maintenance facilities, correct. |  |
| 13 | Fault finding procedure test, correct. |  |
| 14 | Performance parameters including response times, correct. |  |
| 15 | Self test & field module isolation facilities, correct. |  |
| 16 | 24 hour system error test correct. |  |
| 17 | Spares availability, correct. |  |
| 18 |  |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/16 – Checklist for Control Console/ Indicator Diagram |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Control Console/ Indicator Diagram |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Faceplate correct, VDU layout, symbols correct. |  |
| 3 | Cables, cabling, terminations, correct. |  |
| 4 | Circuit continuity tests, wire/null counts, correct. |  |
| 5 | Insulation tests correct. |  |
| 6 | Local circuit function tests correct (alarms, indications, controls). |  |
| 7 | Correspondence through tests correct. |  |
| 8 |  |  |
| 9 |  |  |
| 10 |  |  |
| 11 |  |  |
| 12 |  |  |
| 13 |  |  |
| 14 |  |  |
| 15 |  |  |
| 16 |  |  |
| 17 |  |  |
| 18 |  |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/17 – Checklist for Location |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Location |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Racks, mountings, labelling, equipment positions, correct. |  |
| 3 | Cables, cabling, terminations, correct. |  |
| 4 | Ventilation, cooling, separation heat sensitive/heat producing equipment, correct. |  |
| 5 | Water proof, dust proof, fire proof, rodent proof, vandal resistant, correct. |  |
| 6 | Earthing correct. |  |
| 7 | Circuit continuity tests, wire/null counts correct. |  |
| 8 | Insulation tests, correct. |  |
| 9 | Local circuit function tests correct. |  |
| 10 | Through circuit tests, correct. |  |
| 11 | Local interlocking, test correct. |  |
| 12 | Power supplies correct. |  |
| 13 | Spares availability, correct. |  |
| 14 | Spare space, correct. |  |
| 15 | Telephones operation, telecommunications equipment, correct. |  |
| 16 | Padlocks, locks, fitted & correct. |  |
| 17 | Access correct. |  |
| 18 | Central Interlocking, Function Test to Control Tables, correct. |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/18 – Checklist for Computer Based Interlockings |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Computer Based Interlockings |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Equipment types & configurations & installation physically correct to specifications/ drawings |  |
| 2 | Type approved for intended use. |  |
| 3 | Software versions correct. |  |
| 4 | Hardware correct. |  |
| 5 | All checksums correct. |  |
| 6 | Software simulation test correct. |  |
| 7 | Installed software matches tested software. |  |
| 8 | All system interfaces test correct. |  |
| 9 | Response times correct. |  |
| 10 | Other performance criteria correct. |  |
| 11 | Function test to Control Tables correct. |  |
| 12 |  |  |
| 13 |  |  |
| 14 |  |  |
| 15 |  |  |
| 16 |  |  |
| 17 |  |  |
| 18 |  |  |
| 19 | Occupational Health & Safety/Environmental compliance, correct |  |
| 20 | Workmanship to best practice, equipment in good condition |  |
| 21 | Redundant equipment securely inoperative, made safe/removed. |  |
| 22 | Ready for commissioning into use. |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 13/20 – Checklist for Aspect Sequence |
| --- |
|  | Certificate No: |  |
| Project: |  |  | Prepared By: |  |
| Location / Description: |  |  | Work Package No: |  |
| Specifications and Drawings: |  |  | Date: |  |
| Apparatus: | Aspect Sequence |  | Number/ Name: |  |  | Standard: |
| Type Name: |  |  | Type Classification: |  |  | ESC-21-03 |
| No | Inspection/Test Performed: Equipment/Labelling/Installation/Operation Correct | Initials |
| 1 | Aspect correct and Aspect Sequences correct for the following signals. |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |
| 7 |  |  |
| 8 |  |  |
| 9 |  |  |
| 10 |  |  |
| 11 |  |  |
| 12 |  |  |
| 13 | Aspects correct for the following existing signals at interfaces: |  |
| 14 |  |  |
| 15 |  |  |
| 16 |  |  |
| 17 |  |  |
| 18 |  |  |
| 19 |  |  |
| 20 |  |  |
| 21 |  |  |
| 22 |  |  |
| Remarks |
| Work Status Statement | Received/Checked/Action Statement |
| The Work described above have been performed and recorded in accordance with the specified standard. |  |
| Name: |  | Name: |  |
| Position: |  | Position: |  |
| Signature: |  | Signature: |  |
| Date: |  | Date: |  |

| ITF 14 – Measuring Instrument/Tool Calibration/Test Record |  | No: |  |
| --- | --- | --- | --- |
| Instrument / Tool Type | Serial No. | Calibration / Test Correct |
|  |  | Name | Signature | Date |
| Instrument / Tool Type | Serial No. | Repairs Required |

Interface Coordination Plan

| Interface Coordination Plan – Signalling Work |
| --- |
| Interface Coordination Plan |
| In addition to the provisions included in the Project Works Interface Agreement this Plan nominates personnel and interface matters between the parties. |
| Design Job No: |  |  | Work Description/ Location: |  |  | Interface Coordination Plan Version: |  |
| 1. | Regional Signal Representative | Name: |  | Contact details: |  |
| 2. | Regional Maintenance Engineer | Name: |  | Contact details: |  |
| 3. | Network Control Systems Representative | Name: | N/A? | Contact details: |  |
| 4. | Track Work Representative | Name: |  | Contact details: |  |
| 5. | Electrical Representative | Name: |  | Contact details: |  |
| 6. | Commissioning Manager Signalling | Name: |  | Contact details: |  |
| 7. | Other: | Name: |  | Contact details: |  |
| 8. | Other: | Name: |  | Contact details: |  |
| Program activities requiring Notification, Witness or Hold Points: Examples follow |
| Milestone/Activity Description | Who | N = Notify | W = Witness | H= Hold |
| 1. | Configuration Approval | R R |  |  | H |
| 2. | Detailed Site Survey Approval | Metro Div |  |  | H |
| 3. | Site Integrity Agreement provisions | R R & M E |  |  | H |
| 4. | Installation Work Package | R R |  |  | H |
| 5. | Trench Backfill inspection | R R |  | W |  |
| 6. | ULX / Track Restoration | Track Rep |  | W |  |
| 7. | Other |  |  |  |  |
| 8. | Pre-pour inspections | R R | N |  |  |
| 9. | Other |  |  |  |  |
| 10. | Commissioning Work Package | R R |  |  | H |
| 11. | Other |  |  |  |  |
| 12. | Practical Completion – minor defects | R R |  |  | H |

| Interface Identification |
| --- |
| Does the project have management and/or functional interfaces to other areas? |
|  | Signal Design |  | Control Systems |  | Communications |
|  | Engineering |  | Track |  | Electrical |
|  | Operations |  | Train Crew |  | Station Staff |
|  | Other: |  |  | Other: |  |  | Other: |  |
| Details of the actions required across each interface are to be included in the Interface Management Plan sections of this Plan |
| Site Integrity Agreement and Site Assessment |
| The parties are to assess the condition of existing infrastructure, interface locations and signalling equipment in the vicinity of the works. |
| Are pre-existing spare cables/cores to be utilised by this project? |  | Yes | If yes, detail any conditions: |
|  |  | No | Enter detail here as applicable |
| Is any pre-existing equipment to be utilised / reused by this project? |  | Yes | If yes, detail any conditions: |
|  |  | No | Enter detail here as applicable |
| Will there be redundant material as a result of this project? |  | Yes | If yes, detail any disposal requirement: |
|  |  | No | Enter detail here as applicable |
| Is there any other signal jobs current at the location or for which the submission of “Certified Office Copies” (COC) is outstanding? |  | Yes | If yes, detail: |
|  |  | No | Enter detail here as applicable |
| Is there any new or altered signal design for the area not yet updated to Maintenance Copies? |  | Yes | If yes, detail: |
|  |  | No | Enter detail here as applicable |
| When more than one signalling alteration is being performed in a location, the Regional signal representative is to ensure that the accountability for all the work in that location is clearly allocated to one Commissioning manager |  | Yes | Details and Name: |
|  |  | No | Enter detail here as applicable |
| Has the assessment identified any requirements for track, civil or electrical infrastructure particularly associated with access, reliability and / or maintainability of the signalling infrastructure. |  | Yes | If yes, detail the requirement: |
|  |  | No | Enter detail here as applicable |
| Will the staging of the work require temporary detection to be fitted to out of use points requiring cyclic maintenance? |  | Yes | If yes, Asset engineer to arrange configuration changes, Signal manager to arrange scheduled maintenance. |
|  |  | No | Enter detail here as applicable |
| Where the new and altered signalling work is associated with scope included in a Project Work Interface Agreement agreed between the Region and another project manager eg. Track, civil, electrical or other 3rd party, the agreement shall include development / implementation of a signalling specific Interface Coordination Plan. |  | Yes | Include the responsible 3rd party project manager in the sign off of this interface coordination plan. |
|  |  | No | Enter detail here as applicable |

| Site Integrity Agreement and Site Assessment (continued) |
| --- |
| Is there any transfer of responsibilities from the region associated with authority to excavate, supervision and provision and maintenance of signalling, communications, and services search information |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| Has the “Electrical risk Assessment” identified any hazards and agreed on precautions to be adopted and responsibilities? |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| Where signals are being converted to LED type – has the inspection revealed any read through issues and precautions to be adopted |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| Details of insulation records are to be advised by the Region, particularly known defects. |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| Is there any "other works agreed to be concurrently implemented in the location / s |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| Due to the large scale of change-overs for this job the Regional representative agrees that a minimal portion of the wire disconnection’s may be completed following the “booking into use” |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| The Regional signal representative authorises work to commence in the following location / s |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |
| Other |  | Yes | If yes, provide details: |
|  |  | No | Enter detail here as applicable |

Is there any other site integrity issue to be considered as part of this project? If so, detail:

| Signalling Access Arrangements |
| --- |
| Access to relay room / location permitted between: |  | 00:00 – 00:00 on weekdays, any time on weekends |
|  |  | Other: Click here |
| Special access required (eg. Electronic token): |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Material to be stored on-site: |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Notes: |
| Operational Issues |
| Are there any operational issues to be managed by the project? |  | Yes |
|  |  | No |
| List – including responsibility assignment: |
| Regional Signalling Representative |
| For each signalling works project the Asset engineer, signals (or as otherwise nominated) shall perform the following activities in the capacity of Regional signal representative: Provides a single point gateway between the project and the region, progresses, monitors and reports on internal metropolitan division aspects of the required processes Distribution and control of project design documentation Provide interface coordination within the Metropolitan division for project matters Review and approve in principle - minor work, installation and commissioning work packages Collaborate and manage the provision of track possessions, including rail traffic coordination and provision of test locomotives and SAFE Notices Attend regular project review meetings Attend the pre-and post commissioning meetings Other duties as nominated as follows: |
| The Commissioning Manager shall update Project Explorer on a monthly basis. Nominate any other reporting requirements for this project. If so, detail: |
| Training Requirements |
| Are there any operational issues to be managed by the project? |  | Yes |
|  |  | No |
| List – including responsibilities: |

| Configuration Control |
| --- |
| The Asset engineer, signals shall: Raise the CCR if required for this project Inform the Commissioning manager if any further configuration documentation is required Inform the Commissioning manager when the configuration changes have been approved Ensure that applicable Ellipse application is updated to reflect any changes resulting from this project Close out CCR processes Note that no site works will commence until the Commissioning manager has been formally notified that the configuration changes (if applicable) have been formally approved by the CCB. The Commissioning managerr shall: Assist the Asset engineer, signals with the configuration change process as required Ensure that any site work does not commence until the configuration changes have been approved by the CCB Provide the Asset engineer, signals with a listing of new, altered and removed assets |
| This list shall be provided not less than weeks prior to commissioning |
| Type Approvals, Trials or Waivers |
| Is there signalling type approval issues related to this project? |  | Yes |
|  |  | No |
| Does the work include any registered engineering trials or waivers? |  | Yes |
|  |  | No |
| Commissioning the Works - Requirements |
| Is there a requirement for post-commissioning standby cover to be provided by this project? |  | Yes | If yes, detail: |
|  |  | No | Enter detail here as applicable |
| Are there any issues relating to the commissioning of this project? If so, detail: |
| Pre-Existing Safety Issues |
| Is there any employee safety issues, risks and mitigation strategies used by maintenance personnel to be communicated and incorporated in the planning and site safety management system to be utilised by the construction group? |  | Yes |
|  |  | No |
| List – including who is responsible: |

| Signalling Maintenance Responsibility |
| --- |
| Maintenance shall ensure personnel are trained on the use of the equipment being installed, and are competent to work on the new/altered equipment. |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Determining and organising any new or revised holding of spare equipment is the responsibility of maintenance |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Arrange maintenance personnel involvement in the works, ensure familiarity with the scope, and location/s affected by the work and any identification / marking in use to distinguish them |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Post-Commissioning - arrange attendance for follow up activities, eg points adjustments due to track settlement and stand-by. |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Is there any other maintenance responsibilities for the Project? |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Collaborate for the review of work packages |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Collaborate and attend the detailed site assessment inspection and the development of the Site Integrity Agreement |  | Yes | Detail: Enter detail here as applicable |
|  |  | No |  |
| Maintenance Documentation |
| The documentation requirements relating to the construction, commissioning and handover are covered in this section of the document. From the commencement of electrical construction, a circuit book shall be left on site at a location specified below. This circuit book shall be left on site until commissioning. The circuit book shall be left at: |
| Is there any other maintenance documentation issues relating to this project (such as stage-work)? If so, detail: |

| Documentation and Handover Schedule |
| --- |
| Documentation shall be provided to the Regional representative as specified below: |
| Interim Maintenance Circuit Books |
|  | On Commissioning: | No. Copies: |  | Location: |  |
|  | Next Business Day: | No. Copies: |  | Location: |  |
|  | On Commissioning: | New Track History cards, copies of FPL/Detection and TC forms |
|  | Other: |  |
| Handover Package | 14 days or Other: |  |
| Signed COC Circuit Book/Signal Plan/TIP: | 28 days or Other: |  |
| Construction Documents | Required? |
|  | As Built | Detailed Site Survey Drawings |  | Yes |
|  |  |  |  | No |
|  | As Built | Signal Sighting Forms |  | Yes |
|  |  |  |  | No |
|  | As Built | Installation Drawings |  | Yes |
|  |  |  |  | No |
|  | As Built | Structures and Buildings |  | Yes |
|  |  |  |  | No |
|  | As Built | Mechanical Drawings |  | Yes |
|  |  |  |  | No |
|  | As Built | Level Crossing Layout Plans |  | Yes |
|  |  |  |  | No |
|  | As Built | Clearance Diagrams |  | Yes |
|  |  |  |  | No |
|  | As Built |  |  | Yes |
|  |  |  |  | No |
|  | As Built |  |  | Yes |
|  |  |  |  | No |
| Handover Documentation Package |
| The Handover Documentation Package shall include copies of the following: IBA Forms Commissioning Certificate Copies of new Track History Cards and TC Forms |
| Is there any other documentation required as part of the handover package? (Eg. Copy of work package, manufacturer certificates, equipment manuals, etc.) Other: Other: |

| Checklist from the Inspection and Testing Specifications |
| --- |
| Spec / Clause | Summary of Requirement | Applicable | Spec / Clause | Summary of Requirement | Applicable |
| ESC-21-01 Cl 5.1. | Project Work Interface Agreement to be agreed |  | Yes | ESC-21-02 Cl 4.2.1 | Detailed Site surveys to be GIS / CAD |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-01 Cl 6.1. | Accuracy of existing designs at interfaces, consult Commissioning manager re - status. |  | Yes | ESC-21-02 Cl 4.2.1 | Detailed Site surveys to be Interim to GIS / CAD |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-01 Cl 6.1. | Consult and agree with the Tester in Charge re–safe access to equipment |  | Yes | ESC-21-02 Cl 5.2 | NAN advertising to be arranged by Regional Representative in collaboration with Commissioning manager |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-01 Cl 6.7. | Regional Rep to collaborate for the provision of track possessions, SAFE Notices, NAN, Test Locomotives, Arrange for follow up maintenance activities post Commissioning |  | Yes | ESC-21-02 Cl 6.1 & 6.2 | Maintenance of equipment registers is the responsibility of the Regional asset manager / engineer with information provided by the Commissioning manager |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-01 Cl 6.7. | Regional representative to approve in principle the Installation and Commissioning (or Minor Works) Packages |  | Yes | ESC-21-02 Cl 6.2 | Asset registers, Regional signal representative to provide details of the format. |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-01 Cl 6.7. | Collaborate the implementation of the works with the regional personnel |  | Yes | ESC-21-02 Cl 8.1 | Regional representative to agree that work may be documented in a Minor Work Package |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-02 Cl 2.1. | A job status review including status of other modifications/jobs issued for the area to be conducted |  | Yes | ESC-21-03 Cl 1.6 | The Regional signal representative shall ensure that an Interface Coordination Plan and a Project Work Interface Agreement are agreed with all Regional stakeholders prior to authorising site work to commence |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-02 Cl 2.7. | Signal design shall be issued via the Regional signal representative |  | Yes | ESC-21-03 Cl 1.6 | The Regional signal representative and the Commissioning manager are responsible for updating Interface Coordination Plan during the project lifecycle |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-02 Cl 2.7. | Commissioning manager shall return all design via the Regional signal representative |  | Yes |  |  |  | Yes |
|  |  |  | No |  |  |  | No |
| ESC-21-02 Cl 2.7. | The Regional signal representative shall distribute interim maintenance copies to the required maintenance locations |  | Yes |  |  |  | Yes |
|  |  |  | No |  |  |  | No |
| Requirements may be further detailed in the following NOTES section |

| Interface Management Plan – Signalling and Network Control Systems |
| --- |
| Activity | Details of Agreement | Required? | Activity | Details of Agreement | Required? |
| Regional Rep Design Coordination | Regional Rep to coordinate/ Other: |  | Yes | Network Control Systems |  |  | Yes |
|  |  |  | No |  |  |  | No |
| Progress report to Regional Rep | Requirement: |  | Yes | Network Control Systems | To attend Management Meetings as required |  | Yes |
|  |  |  | No |  |  |  | No |
| Regional Rep Management Meetings | To occur every ( ) Weeks |  | Yes | Network Control Systems | Inspection and Testing Certification Documentation requirements: |  | Yes |
|  |  |  | No |  |  |  | No |
| Regional Rep Services Searches | To be provided by region |  | Yes | Network Control Systems | Commissioning coordination and resource sharing requirements |  | Yes |
|  |  |  | No |  |  |  | No |
| Regional Rep Detailed Site Surveys | Update existing as supplied by regional Rep OR/ |  | Yes | Network Control Systems | Stand by requirements |  | Yes |
|  |  |  | No |  |  |  | No |
| Regional Rep Detailed Site Surveys | New to be produced to GIS Standards OR/ |  | Yes | Network Control Systems | Other |  | Yes |
|  |  |  | No |  |  |  | No |
| Regional Rep Detailed Site Surveys | New to be produced using AutoCad |  | Yes |  |  |  | Yes |
|  |  |  | No |  |  |  | No |
|  |  |  | Yes |  |  |  | Yes |
|  |  |  | No |  |  |  | No |
|  |  |  | Yes |  |  |  | Yes |
|  |  |  | No |  |  |  | No |
|  |  |  | Yes |  |  |  | Yes |
|  |  |  | No |  |  |  | No |
| Requirements may be further detailed in the following NOTES section |

| Interface Management Plan – Others |
| --- |
| Activity | Details of Agreement | Required? | Activity | Details of Agreement | Required? |
| Electrical, Power and Lighting | New supply points, |  | Yes | Track, Track work | Other |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Power and Lighting | Upgrading of new supply points |  | Yes | Civil, Civil work | Embankment widening and drainage work |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Power and Lighting | Other |  | Yes | Civil, Civil work | Roadways and access points |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Traction supply | Air gap locations |  | Yes | Civil, Civil work | Level Crossing arrangements |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Traction supply | Overhead wiring clearances |  | Yes | Civil, Civil work | Other |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Traction supply | Arrangements at substations and section huts |  | Yes | External Parties - RTA | Approaches and Road markings at Level crossing |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Traction supply | New Overhead wiring Structures |  | Yes | External Service Owners | Approvals, locations, protection and supervision for services on ARTC Land |  | Yes |
|  |  |  | No |  |  |  | No |
| Electrical, Traction supply | Other |  | Yes | External Service Owners | Other |  | Yes |
|  |  |  | No |  |  |  | No |
| Track, Track work | New track Infrastructure, |  | Yes | Others |  |  | Yes |
|  |  |  | No |  |  |  | No |
| Track, Track work | Track drainage & reconditioning requirements – track circuit reliability |  | Yes | Others |  |  | Yes |
|  |  |  | No |  |  |  | No |
| Track, Track work | Points - new and reconditioning requirements |  | Yes | Others |  |  | Yes |
|  |  |  | No |  |  |  | No |
| Requirements may be further detailed in the following NOTES section |

Notes

Notes

| Interface Coordination Plan Agreement |
| --- |
| The works are authorised to proceed recognising the provisions set out in this Interface Coordination Plan: |
| Submitted by Commissioning Manager: |
| Name: |  |
| Signature: |  |  | Date: |  |
| Agreed by Regional Signalling Representative: |
| Name: |  |
| Signature: |  |  | Date: |  |
| Agreed by Signal Manager: |
| Name: |  |
| Signature: |  |  | Date: |  |
| Agreed by Network Control Systems: |
| Name: |  |
| Signature: |  |  | Date: |  |
| Agreed by Electrical Representative: |
| Name: |  |
| Signature: |  |  | Date: |  |
| Agreed by Track Representative: |
| Name: |  |
| Signature: |  |  | Date: |  |
| Agreed by Other: |
| Name: |  |
| Signature: |  |  | Date: |  |

Typical Signal Sighting Forms

See ESC-04-01 Signal Sighting and Position

Level Crossing Sighting Forms

| Level Crossing Site Inspection Form |
| --- |
| Level Crossing at: |  |  | Date/Time of Inspection: |  |
| Location: |  |  | Safety Brief Carried Out: | Yes / No |
| Street/Rd/Hwy: |  |  | Rail km: |  |
| Non-Frangible Items: | ( ) | Fog: | ( ) |
| Consider | Comments / Issues |
| Signage |  |
| Line Marking |  |
| Vegetation |  |
| Visual Constraints |  |
| Speed of Traffic |  |
| Volume of Traffic |  |
| Road Upgrading |  |
| Position of Hut |  |
| Road Conditions |  |
| With reference to this form and notes, the undersigned have agreed on the number and position of Advanced Warning Lights and / or alternative improvement to crossing active protection as applicable. |
| Organisation | Name | Signature | Position | Date |
| Uncontrolled when printed |

| Level Crossing Site Inspection |
| --- |
| Location: |  |  | Road Name: |  |  | Kilometrage: |  |
| Note: Sketch to be attached |
| Sydney Side Configuration | Country Side Configuration |
| Lights | Required (Yes/No) | Focal Distance | Lights | Required (Yes/No) | Focal Distance |
| E, F |  |  | A, B |  |  |
| G, H |  |  | C, D |  |  |
| Additional – same post |  |  | Additional – same post |  |  |
| Additional – new post |  |  | Additional – new post |  |  |
| Advance Warning Lights |  |  | Advance Warning Lights |  |  |
| Miscellaneous |
| Line Speed Up Direction |  | Line Speed Down Direction |  |
| Automatic Approach (Yes/No) |  | “B” Double Road Traffic (Yes/No) |  |
| Track Shunt Conditions (Poor/Good) |  | Track Ballast Condition (Poor/Good) |  |
| Booms Required - Type (Yes/No) |  | Booms Down – Bell Off (Sydney side/Country side) |  |
| Bell Timer Required (Yes/No) |  | Shunters Pushbuttons (Yes/No) |  |
| Number of and Type of Rail Traffic |  | Shunt Enhancement Required (Yes/No) |  |
| Power Supply Arrangements |  | Existing Track Circuit Type |  |
| Name: |  |  | Signature: |  |  | Position: |  |  | Date: |  |
| Uncontrolled when printed |

| Stakeholder Site Inspection and Authority to Commission |
| --- |
| In relation to the level crossing installation works at: |  |
| Work Package No.: |  | and in accordance with drawings: |
| A site inspection has been carried out with outstanding issues to be added as indicated in the following table: |
| Outstanding Issues | Action By | By Date |
| The following representatives acknowledge that the requirements of their respective organisations have been met, with the exception of any outstanding items as listed above, and give authority for commissioning of the works. |
| Organisation | Name | Signature | Position | Date |
| Uncontrolled when printed |

| Gated Pedestrian Crossing Assessment Sheet |
| --- |
| Crossing Location: |  |  | Date Visited: |  |
| Name of Inspector: |  |  | Sheet 1 of 3 |
| Assessment Criteria | Yes | No |
|  | How many tracks? Mark up sketch | One | Two | Three | Four |  |  |
|  | Is the crossing used for station access? |  |  |
|  | Is the crossing located immediately adjacent to a road crossing? |  |  |
|  | Is the crossing located on an obviously curved section of track or a crossover? |  |  |
|  | Does the corral layout significantly differ from that shown & if so, mark up sketch? |  |  |
|  | Is the crossing perpendicular to track? If not, mark approximate angle on sketch. |  |  |
|  | Have you marked all critical base dimensions in either the table shown overleaf or on the sketch? |  |  |
|  | On sketch, mark in the installed signage & positions. Signage may not need to be the latest version shown, but it does need to fulfil the intent shown. |  |  |
|  | Are there contrasting delineation strips along both edges of the crossing? |  |  |
|  | Are there tactile strips along both edges of the crossing? |  |  |
|  | What is the surface over the track made of: | Concrete | Asphalt | Timber | Other |  |  |
|  | What are the type of sleepers under the crossing? | Concrete | Timber |  |  |
|  | Is the pathway over the tracks relatively flat with no significant trip hazards? |  |  |
|  | Is there super elevation between far rails of more than ~50mm? |  |  |
|  | Is the widest flange gap in the walking surface wider than 75mm? |  |  |
|  | Does either pathway leading up to the tracks ramp downwards towards the track? |  |  |
|  | Is there a permanent opening as per dimension ‘C’ between the fully open motorised gate and the emergency exit fencing, of at least 850mm? |  |  |
|  | Is the fencing associated with the crossing generally in good condition? |  |  |
|  | What are the walking surfaces in the corrals made of? | Concrete | Asphalt | Timber | Other |  |  |
|  | What are the walking surfaces leading up to the corrals made of: | Concrete | Asphalt | Timber | Other |  |  |
|  | Are there any steps incorporated into the access path leading up to the crossing? |  |  |
|  | Is some form of area lighting provided over the tracks and corrals. |  |  |
|  | Is some form of area lighting provided on pathways leading up to the corrals. |  |  |
|  | Are both ‘don’t walk’ lights and both tone generators provided and functioning. |  |  |
|  | Are tactile pads provided at gates as shown on the sketch. |  |  |
|  | Are the emergency exit gates fitted with a latch. |  |  |
|  | Are the emergency exit gates fitted with functional spring close hinges. |  |  |
|  | Is the motorised gate leaf fitted with chevron warning tape. |  |  |
|  | Does the motorised gate have a rubber buffer strip on the leading edge. |  |  |
| If a question is not applicable, write N/A If associated with a road crossing and there are two pedestrian crossings, fill out two separate forms. Identify which side of the road the crossing is located on. |
| Comments |
| Uncontrolled when printed |
| SKETCH UP CROSSING USING GRID BELOW |

| Gated Pedestrian Crossing Assessment Sheet | Sheet 2 of 3 |
| --- | --- |
| Scale 300mm grid |

| Gated Pedestrian Crossing Assessment Sheet | Sheet 3 of 3 |
| --- | --- |

| Level Crossing Location Maintenance Visit Sheet |
| --- |
| Location: |  |  |
| Date of Visit |  |  |  |  |  |  |  |  |  |
| Charge Current (A) (500ma into Battery) |  |  |  |  |  |  |  |  |  |
| Float voltage (V) |  |  |  |  |  |  |  |  |  |
| Under voltage Alarm (V) (12.2V – 10 Cell or 14.64V – 12 Cell) |  |  |  |  |  |  |  |  |  |
| MR6 Diode Check |  |  |  |  |  |  |  |  |  |
| Electrolyte Level |  |  |  |  |  |  |  |  |  |
| Lamp Voltage SS & CS (6 Monthly) |  |  |  |  |  |  |  |  |  |
| Operating Load Current (A) |  |  |  |  |  |  |  |  |  |
| Voltage of Cells Under Load (Lowest Cell & Battery Voltage) After 2 Minutes Operation |  |  |  |  |  |  |  |  |  |
| Earth Leakage (AC) Active & Common Bus |  |  |  |  |  |  |  |  |  |
| Earth Leakage (DC) Positive and Negative Bus |  |  |  |  |  |  |  |  |  |
| Alignment of Lamps |  |  |  |  |  |  |  |  |  |
| Lamp Changeout |  |  |  |  |  |  |  |  |  |
| Monitor |  |  |  |  |  |  |  |  |  |
| Remarks |  |  |  |  |  |  |  |  |  |
| Signature |  |  |  |  |  |  |  |  |  |

# Text boxes

TRACK 1